## 1. INTRODUCTION
STEAM SYSTEM SCOPING TOOL | 2000-10-17
evaluation version 1.0b
INTRODUCTION
AUDIENCE FOR THE TOOL | The audience for this tool is steam system energy managers and steam system operations personnel for large industrial plants - from industries noted by the Department of Energy (DOE) as "Industries of the Future." The Department of Energy's nine Industries of the Future are Agriculture, Forest Products, Mining, Aluminum, Glass, Petroleum, Chemicals, Metal Casting and Steel.
PURPOSE OF THE SCOPING TOOL | Using this Tool will assist you to:
a) Develop a greater awareness of opportunities to improve your steam system;
b) Allow you to evaluate your steam system operations against identified best practices; and
c) Compare your steam system operations to those from other facilities (by comparing responses to the various Scoping Tool questions).
WHAT IS INCLUDED IN THIS TOOL | The Steam System Scoping Tool includes seven worksheets:
1. Introduction
2. Steam System Basic Data
3. Steam System Profiling
4. Steam System Operating Practices - Total Steam System
5. Steam System Operating Practices - Boiler Plant
6. Steam System Operating Practices - Distribution, End Use, Recovery
7. Summary Results
HOW TO USE THE STEAM SCOPING TOOL | Access Each Worksheet by clicking on the appropriate worksheet label at the bottom of the screen. For example, click on the "Steam System Basic Data" tab to access that worksheet.
Start by Choosing a File Name for your spreadsheet, and Save a copy of the spreadsheet using that name.
Answer the questions in Worksheet #2 - Steam System Basic Data.
Provide scores for your steam system in Worksheets #3 through #6. Each of the questions in these four worksheets has a number of possible scores. Enter your appropriate score in the correct worksheet cell.
Once you have entered your scores in Worksheets #3 through #6, go to Worksheet #7 - Summary Results to see a summary of the scores that you entered.
Finally, Save a copy of your completed spreadsheet and Print copies of any of Worksheets #2 through #7 that you would like paper copies of.
HOW YOU CAN USE YOUR RESULTS | Review Results - Are there any areas where you can make obvious improvements to your steam system?
Share Results - Share what you learned from using this tool with your co-workers and your management. Look for opportunities to identify improvement projects based on your results.
Compare Results - DOE plans to collect results from many plants and publish them on the BestPractices Steam web site - so you can compare what you have found for your system with results obtained for other operations.
Redo Your Survey At A Later Date - Redoing the survey can show that you have made improvements, or maintained the improvements that you previously made.
HOW DOE WILL USE YOUR RESULTS | The DOE requests that you provide the results of your survey to them. They plan to create a database of responses to the Steam Scoping Tool questions, and the summary information from this database will be available on the BestPractice Steam website and can be made available to anyone who requests it. You will then be able to compare your individual results to results from all respondents and from similar type industrial plants.
Confidentiality Of Your Input - DOE will insure that if you provide them with there results from your survey, the results will be held strictly confidential. DOE will also not release your contact information to any third party service providers, so you can be sure that there will be no follow-up as a result of you providing your results to them.
HOW TO SUBMIT YOUR RESULTS | When you complete this survey, you can submit your results to:
Anthony Wright, Oak Ridge National Laboratory
phone until 11/15/00: 865-574-6878
phone after 11/15/00: 865-946-1353
email: wrightal@ornl.gov
THANK YOU!! | We appreciate your interest in completing this survey, and hope that you will provide your results to us so that we can develop a database of responses useful to Steam System Users.
ACKNOWLEDGEMENT | The Steam System Scoping Tool was developed by the DOE BestPractices Steam effort, a part of the DOE Office of Industrial Technologies. Thanks to all of the members of the BestPractices Steam Best Practice and Technical subcommittee for reviewing early versions of the tool and providing their useful input to its development.

## 2. STEAM SYSTEM BASIC DATA
| STEAM SYSTEM SCOPING TOOL, evalation version 1.0b | 2000-10-17
STEAM SYSTEM BASIC DATA
BASIC DATA ABOUT YOUR SYSTEM
What To Do Document some of the basic operating information about your steam system.
Why Important Documenting basic steam system data is important to help you to understand your steam system and to identify potential areas for improving your steam operations.
ANSWERS TO BASIC DATA QUESTIONS
a | Briefly describe the type of production that your plant does in the column to the right. If you know the Standard Industrial Code (SIC) for your plant operations, please include that in your description.
IF YOU CONSUME STEAM BUT DO NOT GENERATE ANY OF YOUR OWN, PLEASE SKIP TO QUESTION "h"
ANSWERS TO BASIC DATA QUESTIONS
b | What Is Your Total Annual Steam Production? |  | MMlb/year
c | How Many Hours Per Year Is Your System In Operation? |  | hours
d | What Is Your Total Steam Generation Capacity? |  | 1000 lb/hour
e | What Is Your Average Steam Generation Rate? |  | 1000 lb/hour
f | What Is The % Distribution (On A Btu Basis) Of Your Fuel Sources For Steam Generation?
| Coal |  | %
| Fuel Oil (#6) |  | %
| No. 2 Fuel Oil |  | %
| Natural Gas |  | %
| Process Waste Heat |  | %
| Biomass |  | %
| Solid Wastes |  | %
| Other |  | %
| TOTAL (Should add up to 100%) | 0 | %
g | Do You Measure Any Of The Following (answer yes or no)?
Fuel input
Steam production
Feedwater Flow
BFW makeup water flow
Flue gas temperature
h | Do You Have Any Heat Engines On Site?
Back Pressure Steam Turbines
Number
| Total Capacity |  | kW
Condensing Steam Turbines
Number
| Total Capacity |  | kW
Combustion Gas Turbines Without HRSG
| Total Capacity |  | kW
Combustion Gas Turbines With HRSG
| Total Capacity |  | kW
Other (specify type)
| Total Capacity |  | kW
i | How Much Steam Do You Buy Annually From Others? |  | MMlb/year
j | How Many Steam Traps Do You Have In Your Steam System?
k | What is Your Average Boiler Blowdown Rate? |  | lb/hour

## 3. STEAM SYSTEM PROFILING
| STEAM SYSTEM SCOPING TOOL, evaluation version 1.0b | 2000-10-17
STEAM SYSTEM PROFILING
STEAM COSTS
What To Do Identify what it costs at your facility to produce steam (in units of $/1000 lbs), and use this as a benchmark for evaluating opportunities for improving your steam operations. Start with determining what your fuel costs are to make steam, then add other costs associated with your operations (chemical costs, labor, etc).
Why Important Understanding the cost to make steam can be an eye-opener - producing steam is not free! Any opportunity that reduces the amount of steam generated saves money, so understanding the cost to make steam is a key step to being able to quantify improvement opportunities.
YOUR
|  | ACTIONS | SCORE | SCORE
SC1 | Do you monitor your Fuel Cost To Generate Steam - in terms of ($) / (1000 lbs. of steam produced)? | yes | 10
|  | no | 0
SC2 | How often do you calculate and trend your Fuel Cost To Generate Steam? | at least quarterly | 10
|  | at least yearly | 5
|  | less than yearly | 0
STEAM/PRODUCT BENCHMARKS
What To Do Identify how much steam it takes to make your key products. Then track this benchmark: a) with what other facilities in your company do; b) with how your competitors do; and c) with how this benchmark varies in your operations over time.
Why Important The bottom line of your operation is how effectively you make your products, and steam use has an impact on your productivity. Steam/product benchmarking is an excellent way to monitor productivity and how steam improvements translate to improved productivity.
YOUR
|  | ACTIONS | SCORE | SCORE
BM1 | Do you Measure your Steam/Product Benchmark - in terms of (lbs. of steam needed) / (unit of product produced)? | yes | 10
|  | no | 0
BM2 | How often do you Measure and Trend your Steam/Product Benchmark - in terms of (lbs. of steam needed) / (unit of product produced)? | at least quarterly | 10
|  | at least yearly | 5
|  | less than yearly | 0
STEAM SYSTEM MEASUREMENTS
What To Do Identify key steam operational parameters that you should monitor and ensure that you are adequately measuring them.
Why Important You Can't Manage What You Don't Measure! Measurement of key steam system parameters assists you in monitoring your system, diagnosing potential system problems, and ensuring that system improvements continue to provide benefits to your operations.
YOUR
|  | ACTIONS | SCORE | SCORE
MS1 | Do you measure and record Critical Energy Parameters for your Steam System?
| Steam Production Rate (to obtain total steam production) | yes | 10
| Fuel Flow Rate (to obtain total fuel consumption) | yes | 6
| Feedwater Flow Rate | yes | 6
| Makeup Water Flow Rate | yes | 4
| Blowdown Flow Rate | yes | 2
| Chemical Input Flow Rate | yes | 2
|  | no to all of above | 0
MS2 | How intensely do you meter your steam flows? - CHOOSE ONE OF FIVE ANSWERS | by major user/equip | 20
|  | by process unit | 10
|  | by area or building | 5
|  | by plant as a whole | 2
|  | not at all | 0

## 4. SSOP-Total Steam System
| STEAM SYSTEM SCOPING TOOL, evaluation version 1.0b | 2000-10-17
STEAM SYSTEM OPERATING PRACTICES
STEAM TRAP MAINTENANCE
What To Do Implement a comprehensive program to correctly select, test, and maintain your steam traps.
Why Important Steam traps play three important functions: a) prevent steam from escaping from the system before the heat is utilized; b) remove condensate from the system; and c) vent noncondensable gases. Poor steam trap selection, testing, and maintenance can result in many system problems including water hammer, ineffective process heat transfer, steam leakage, and system corrosion. An effective steam trap selection and maintenance program is often an excellent investment with paybacks of less than half a year.
YOUR
|  | ACTIONS | SCORE | SCORE
ST1 | Does Your System Steam Trap Maintenance Program Include The Following Activities?
| Proper Trap Selection For Application | yes | 10
| At Least Annual Testing Of All Traps | yes | 10
| Maintaining A Steam Trap Database | yes | 10
| Repairing/Replacing Defective Traps | yes | 10
|  | none of the above | 0
WATER TREATMENT PROGRAM
What To Do Implement and maintain an effective Water Treatment Program in your steam system.
Why Important An effective steam system Water Treatment Program: a) reduces the potential for waterside fouling problems in your boilers; b) is critical to minimizing boiler blowdown and the resulting energy losses; c) can reduce the generation of wet steam; and d) greatly reduces the potential for corrosion problems throughout your steam system. Most effective water treatment programs include both mechanical (filtration and deaeration) and chemical treatment. Problems in this area can lead to significant plant productivity issues related to equipment failure and downtime - be sure to consult with a chemical treatment specialist on an ongoing basis.
YOUR
|  | ACTIONS | SCORE | SCORE
WT1 | How often do you ensure that your Water Chemical Treatment System is functioning properly? | at least daily | 10
|  | at least weekly | 5
|  | less than weekly | 0
WT2 | How often do you clean Fireside or Waterside deposits in your Boiler? | once a year | 10
|  | every 1-5 years | 5
|  | >5 years | 0
WT3 | How often do you measure Conductivity (or Total Dissolved Solids [TDS]) in your Boiler and determine what your Steam and Mud Drum Blowdown Rate (or Top and Bottom Boiler Blowdown Rate) should be? | once/shift | 10
|  | once/day | 5
|  | once/week | 0
SYSTEM INSULATION
What To Do Ensure that the appropriate major components of your steam system are well insulated. Determine the economic insulation thickness for your system components, and perform system insulation surveys to identify exposed surfaces that should be insulated and/or unrestored or damaged insulation.
Why Important Effective insulation - on piping, valves, fittings, and vessels - serves many important purposes. Insulation keeps steam energy within the system to be effectively used by processes, it can reduce temperature fluctuations in the system, it can reduce space conditioning requirements, and it can reduce the potential for personnel burns.
YOUR
|  | ACTIONS | SCORE | SCORE
IN1 | Is your Boiler Plant equipment insulation (refractory, piping, valves, flanges, vessels, etc.) maintained and in good condition? | yes | 10
|  | no | 0
IN2 | Is your Steam Distribution, End Use, and Condensate Recovery equipment insulation (piping, valves, flanges, heat exchangers, etc.) maintained and in good condition? | yes | 20
|  | no | 0
STEAM LEAKS
What To Do Identify and quickly repair steam leaks in your steam system.
Why Important Steam leaks can result from failures associated with such things as improper piping design, corrosion problems, and valve failures. In high-pressure industrial steam systems, energy costs associated with steam leaks can be substantial. Identifying and repairing steam leaks is essential to properly balancing your steam system.
YOUR
|  | ACTIONS | SCORE | SCORE
LK1 | How often do you experience Steam Leaks in your Steam System? | < once in 6 months | 10
|  | once in 1-6 months | 5
|  | > once a month | 0
WATER HAMMER
What To Do Detect and quickly eliminate Water Hammer in your steam system.
Why Important Water Hammer is a serious concern - it can lead to failure and rupture of piping and valves, and in many cases significant personnel injury due to contact with steam and condensate. There are two main types of water hammer: one caused by accumulation of condensate in steam distribution piping and transport of this condensate by high-velocity steam; and the other caused by a pressure pulse resulting from steam collapse (rapid condensation) in condensate return lines and heat exchange equipment. Water Hammer in your steam system always says FIX ME!!
YOUR
|  | ACTIONS | SCORE | SCORE
WH1 | How often do you detect noticable Water Hammer in your Steam and Condensate Recovery System? | < once in 6 months | 10
|  | once in 1-6 months | 5
|  | > once a month | 0
MAINTAINING EFFECTIVE STEAM SYSTEM OPERATIONS
What To Do Establish and carry out a comprehensive steam system maintenance program.
Why Important Effective steam system operating practices and improvements can provide benefits to your steam operations year after year - IF you have an effective system maintenance program in place. Major areas of maintenance that will provide year-after-year benefits to your operations include: a) steam traps; b) boiler performance; c) water treatment; d) turbines, piping, heat exchangers, pumps, motors, and valves; and e) system insulation.
YOUR
|  | ACTIONS | SCORE | SCORE
MN1 | Do you periodically - at least once a year - inspect the following important Steam Plant Operational Equipment?
| Boiler Plant Equipment - boiler, deaerator, feedwater tank, chemical treatment equipment, blowdown equipment, economizer, combustion air preheater, etc.? | yes | 5
| Distribution System Equipment - piping (including design), steam traps (types, sizes, locations), air vents, valves, pressure reducing stations, etc.? | yes | 5
| End Use System Equipment - turbines, piping (including design), heat exchangers, coils, jacketed kettles, steam traps (types, sizes, locations), air vents, vacuum breakers, pressure reducing valves, etc.? | yes | 5
| Recovery System Equipment - piping (including design), valves, fittings, flash tanks, condensate pumps, condensate meters, etc.? | yes | 5
|  | no to all of above | 0

## 5. SSOP-Boiler Plant
| STEAM SYSTEM SCOPING TOOL, evaluation version 1.0b | 2000-10-17
BOILER PLANT OPERATING PRACTICES
BOILER EFFICIENCY
What To Do Measure, trend, and look for opportunities to improve the efficiency of your boilers.
Why Important One of the key boiler plant functions is to generate steam at the highest possible efficiency. Major sources of boiler efficiency losses include: a) combustion and flue gas energy losses [typically the largest]; b) blowdown losses; and c) refractory insulation losses. It is important to measure and trend boiler efficiency, flue gas temperature, flue gas oxygen content, and flue gas carbon monoxide content on a regular basis. Measurement and control of excess oxygen is critical to minimizing boiler combustion energy losses. Trending flue gas temperature can provide indications of other potential boiler problems, such as waterside or fireside fouling problems.
YOUR
|  | ACTIONS | SCORE | SCORE
BE1 | How often do you measure your Boiler Efficiency - [(heat absorbed by the steam) / (energy input from fuel)]? | at least quarterly | 10
|  | at least yearly | 5
|  | less than yearly | 0
BE2 | Do you measure the following parameters as a function of boiler load and ambient temperature?
| Flue gas temperature | yes | 5
| Flue gas Oxygen content | yes | 5
| Flue gas CO content | yes | 5
|  | no to all of above | 0
BE3 | How do you control Excess Air in your Boiler to maximize Boiler Efficiency? | automatically | 10
|  | manually | 5
|  | not at all | 0
HEAT RECOVERY EQUIPMENT
What To Do Evaluate installation of Heat Recovery Equipment on your Boiler Plant.
Why Important In some boilers, high flue gas temperatures and high continuous blowdown rates can provide opportunities for installation of heat recovery equipment. Feedwater economizers and combustion air preheaters can, under appropriate conditions, be installed to extract excess flue gas energy and effectively increase the boiler efficiency. Blowdown heat recovery equipment can also, for some systems, be installed to extract otherwise lost heat from the blowdown system. For either potential opportunity, an economic analysis is needed to determine the feasibility of the opportunity, and the equipment should be designed and installed by qualified professionals.
YOUR
|  | ACTIONS | SCORE | SCORE
HR1 | Do you have any of the following Heat Recover Equipment installed on your Boilers?
| Feedwater Economizer and/or Combustion Air Preheater | yes | 10
| Blowdown Heat Recovery | yes | 5
|  | no to all of above | 0
GENERATING DRY STEAM
What To Do Ensure that you generate high-quality dry steam in your boiler plant.
Why Important Steam of 100% quality contains no liquid water; wet steam contains liquid droplets. Generating wet steam in your boiler can cause many system problems, including: a) inefficient process heat transfer; b) equipment failure by water hammer; c) equipment failure by corrosion and erosion; and d) steam trap failure by overloading. Some typical causes for creation of wet steam and boiler carryover are: a) wide swings in boiler water level; b) reduced operating pressure; c) boiler overload; and d) poor boiler total dissolved solids (TDS) control. A critical step to ensuring generation of high-quality steam is to measure steam quality out of your boiler; this is typically done using steam calorimeters.
YOUR
|  | ACTIONS | SCORE | SCORE
DS1 | How often do you check the Quality of Steam that is output from your Boiler to the Distribution System, and ensure that you are generating Dry Steam? | at least quarterly | 10
|  | at least yearly | 5
|  | less than yearly | 0
GENERAL BOILER OPERATION
What To Do Ensure that your boilers perform their functions without large fluctuations in operating conditions.
Why Important How you control boiler operation can effect many elements of the steam system - including the operating life of the boiler, the quality of steam produced, and the effectiveness of steam use throughout your production operations.
YOUR
|  | ACTIONS | SCORE | SCORE
GB1 | Do you have an automatic blowdown controller on your Boiler? | yes | 5
|  | no | 0
GB2 | What is the frequency of High Level Alarms (possibly indicating boiler undersized) or Low Level Alarms (possibly indicating boiler oversized) for your Boiler? | less than 1/month | 10
|  | 1-5 per month | 5
|  | more than 5/month | 0
GB3 | How often do you experience steam pressure fluctuations of greater than 10% of your Boiler Operating Pressure? | less than 1/month | 5
|  | 1-5 per month | 3
|  | more than 5/month | 0

## 6. SSOP-Dist, End Use, Recovery
| STEAM SYSTEM SCOPING TOOL, evaluation version 1.0b | 2000-10-17
STEAM DISTRIBUTION, END USE, RECOVERY - OPERATING PRACTICES
MINIMIZE STEAM FLOW THROUGH PRVs
What To Do Investigate potential to replace pressure reducing valves with backpressure turbines in your steam system.
Why Important In many steam systems, pressure reducing valves (PRVs) are used to provide steam at pressures lower than generated from the boiler. A potential opportunity for improving a steam system is to minimize the flow of steam through PRVs. One opportunity for doing this is to replace PRVs with backpressure turbines that can provide the low-pressure steam and generate electricity or shaft power that can be utilized. A detailed economic analysis must be performed to evaluate this type of opportunity.
YOUR
|  | ACTIONS | SCORE | SCORE
PR1 | How do you reduce steam pressure in your steam system? | using backpressure turbines | 10
|  | using boiler control or PRVs | 5
|  | no pressure reduction | 0
RECOVER AND UTILIZE AVAILABLE CONDENSATE
What To Do Determine how much of your available condensate you recover and utilize.
Why Important Returning a substantial portion of your condensate to your boiler can have both energy and chemical treatment benefits: a) condensate is hotter than makeup water, so less energy is required to convert condensate to steam; and b) condensate requires significantly less chemical treatment than makeup water, so there are savings in chemical treatment costs associated with returning condensate. Returning as much condensate as possible also can help to reduce boiler blowdown (because fewer impurities are resident in condensate), and so minimize blowdown energy losses.
YOUR
|  | ACTIONS | SCORE | SCORE
CR1 | How much of your available Condensate do you recover and utilize? | greater than 80% | 10
|  | 40% to 80% | 5
|  | less than 40% | 0
USE HIGH-PRESSURE CONDENSATE TO MAKE LOW-PRESSURE STEAM
What To Do Investigate opportunity to utilize high-pressure condensate to produce useable low-pressure steam.
Why Important An opportunity for utilizing high-pressure condensate is to allow it to pass through a flash tank and utilize the flash steam in low-pressure steam applications. The remainder of the condensate, now at lower pressure and temperature, can then be sent back to the boiler for use in producing steam.
YOUR
|  | ACTIONS | SCORE | SCORE
FS1 | How much of your available Flash Steam do you recover and utilize? | greater than 80% | 10
|  | 40% to 80% | 5
|  | less than 40% | 0

## 7. SUMMARY RESULTS
STEAM SCOPING TOOL, evaluation version 1.0b |  | 2000-10-17
SUMMARY RESULTS
| POSSIBLE | YOUR
SCOPING TOOL QUESTIONS | SCORE | SCORE
1. STEAM SYSTEM PROFILING
STEAM COSTS
SC1 | 10 | 0
SC2 | 10 | 0
STEAM/PRODUCT BENCHMARKS
BM1 | 10 | 0
BM2 | 10 | 0
STEAM SYSTEM MEASUREMENTS
MS1 | 30 | 0
MS2 | 20 | 0
STEAM SYSTEM PROFILING SCORE | 90 | 0
2. STEAM SYSTEM OPERATING PRACTICES
STEAM TRAP MAINTENANCE
ST1 | 40 | 0
WATER TREATMENT PROGRAM
WT1 | 10 | 0
WT2 | 10 | 0
WT3 | 10 | 0
SYSTEM INSULATION
IN1 | 10 | 0
IN2 | 20 | 0
STEAM LEAKS
LK1 | 10 | 0
WATER HAMMER
WH1 | 10 | 0
MAINTAINING EFFECTIVE STEAM SYSTEM OPERATIONS
MN1 | 20 | 0
STEAM SYSTEM OPERATING PRACTICES SCORE | 140 | 0
3. BOILER PLANT OPERATING PRACTICES
BOILER EFFICIENCY
BE1 | 10 | 0
BE2 | 15 | 0
BE3 | 10 | 0
HEAT RECOVERY EQUIPMENT
HR1 | 15 | 0
GENERATING DRY STEAM
DS1 | 10 | 0
GENERAL BOILER OPERATION
GB1 | 5 | 0
GB2 | 10 | 0
GB3 | 5 | 0
BOILER PLANT OPERATING PRACTICES SCORE | 80 | 0
4. STEAM DISTRIBUTION, END USE, RECOVERY OPERATING PRACTICES
MINIMIZE STEAM FLOW THROUGH PRVs
PR1 | 10 | 0
RECOVER AND UTILIZE AVAILABLE CONDENSATE
CR1 | 10 | 0
USE HIGH-PRESSURE CONDENSATE TO MAKE LOW-PRESSURE STEAM
FS1 | 10 | 0
DISTRIBUTION, END USE, RECOVERY OP. PRACTICES SCORE | 30 | 0
SUMMARY OF STEAM SCOPING TOOL RESULTS
| POSSIBLE | YOUR
| SCORE | SCORE
STEAM SYSTEM PROFILING | 90 | 0
STEAM SYSTEM OPERATING PRACTICES | 140 | 0
BOILER PLANT OPERATING PRACTICES | 80 | 0
DISTRIBUTION, END USE, RECOVERY OP. PRACTICES | 30 | 0
TOTAL SCOPING TOOL QUESTIONAIRE SCORE | 340 | 0
TOTAL SCOPING TOOL QUESTIONAIRE SCORE (%) |  | 0%
Date That You Completed This Questionaire